## Summary
HVAC Startup Commissioning Checklist Summary
Indicators are calculated from entered startup checklist records.
Indicator | Calculated Value | Status | Records
Total startup records |  | Complete
Complete checklists |  | Needs Review
Needs human review |  | Open
Open checklists |  | Awaiting Sign-Off
Awaiting sign-off
Reading inputs incomplete
Administrative sign-offs
Checklist completion rate
Earliest startup date
Latest startup date

## Startup Checklist
HVAC Startup Commissioning Checklist
Record observed startup readings and internal checklist decisions for each newly started system.
Orange cells are editable. Calculated alerts require a human check against job and manufacturer information.
Startup ID | Startup Date | Customer | Job / Site | Equipment Description | Equipment Type | Operating Mode | Technician | Responsibility | Outdoor Air (°F) | Return Air (°F) | Supply Air (°F) | Temp Split (°F) | Measured Voltage (V) | Rated Voltage (V) | Running Amps (A) | Nameplate Amps (A) | Suction Pressure (psig) | Liquid Pressure (psig) | Condensate / Drain | Airflow / Rotation | Controls / Thermostat | Pressure / Electrical Review | Admin Sign-Off | Sign-Off Date | Notes | Reading Alert | Checklist Status
DEMO-START-001 | 2026-07-29 | Fictional Cedar Kite School | Demo Classroom Wing | Demo Split System 1 | Split AC | Cooling | Avery Example | Startup Technician | 88 | 75 | 56 |  | 231 | 230 | 12.4 | 18 | 128 | 312 | Complete | Complete | Complete | Complete | Signed Off | 2026-07-30 | Fictional example with recorded cooling readings.
DEMO-START-002 | 2026-08-05 | Imaginary Northstar Studio | Sample Production Room | Example Heat Pump A | Heat Pump | Cooling | Jordan Sample | Installing Contractor | 92 | 76 | 62 |  | 253 | 230 | 20 | 20 | 135 | 340 | Complete | Complete | Complete | Complete | Signed Off | 2026-08-05 | Boundary example at the editable voltage and amp review limits.
DEMO-START-003 | 2026-08-12 | Sample Sunbeam Library | Fictional Reading Room | Demo Rooftop Unit 3 | Rooftop Unit | Cooling | Casey Fiction | Startup Technician | 95 | 78 | 58 |  | 205 | 230 | 17 | 24 | 142 | 356 | Complete | Complete | Complete | Needs Review | Not Ready |  | Human review requested for the recorded voltage.
DEMO-START-004 | 2026-08-18 | Fictional Harbor Lantern Cafe | Demo Dining Area | Example Furnace 2 | Gas Furnace | Heating | Riley Placeholder | Installing Contractor | 35 | 68 | 103 |  | 119 | 120 | 7.2 | 10 |  |  | Complete | Complete | Complete | Complete | Signed Off | 2026-08-18 | Pressure readings are not applicable to this fictional furnace example.
DEMO-START-005 | 2026-08-25 | Imaginary Maple Gear Shop | Sample Assembly Bay | Demo Air Handler B | Air Handler | Fan Only | Avery Example | Startup Technician | 70 | 72 | 72 |  | 240 | 240 | 3.8 | 5 |  |  | Not Applicable | Complete | Complete | Complete | Signed Off | 2026-08-26 | Fan-only startup example.
DEMO-START-006 | 2026-08-31 | Sample Copper Finch Office | Fictional Open Office | Example Packaged Unit C | Packaged Unit | Cooling | Jordan Sample | Installing Contractor | 86 | 74 | 55 |  | 229 | 230 | 15 | 22 | 124 | 305 | Pending | Complete | Complete | Complete | Not Ready |  | Drain observation remains open for a later human check.
DEMO-START-007 | 2026-09-04 | Fictional Juniper Moon Center | Demo Consultation Room | Sample Heat Pump D | Heat Pump | Heating | Casey Fiction | Startup Technician | 42 | 69 | 99 |  | 240 | 240 | 22 | 20 | 110 | 330 | Complete | Complete | Complete | Needs Review | Not Ready |  | Recorded current exceeds the editable review ratio.
DEMO-START-008 | 2026-09-07 | Imaginary Meadow Brick Hall | Sample Meeting Hall | Demo Split System 4 | Split AC | Cooling | Riley Placeholder | Installing Contractor | 84 | 75 | 65 |  | 232 | 230 | 11.5 | 18 | 120 | 298 | Complete | Complete | Complete | Needs Review | Not Ready |  | Temperature split is below the editable cooling review range.
DEMO-START-009 | 2026-09-10 | Sample Blue Acorn Market | Fictional Sales Floor | Example Rooftop Unit 5 | Rooftop Unit | Cooling | Avery Example | Startup Technician | 90 | 77 | 53 |  | 253 | 230 | 18 | 18 | 132 | 325 | Complete | Complete | Complete | Complete | Awaiting Sign-Off |  | Recorded values are at editable review boundaries; sign-off remains open.
DEMO-START-010 | 2026-09-12 | Fictional Silver Pebble Center | Demo Activity Room | Sample Furnace 6 | Gas Furnace | Heating | Jordan Sample | Startup Technician | 40 | 70 | 90 |  | 121 | 120 | 6.5 | 9 |  |  | Complete | Complete | Needs Review | Complete | Not Ready |  | Controls observation requires a human follow-up.

## Assumptions
Startup Checklist Assumptions and Editable Lists
These internal review prompts are editable and do not replace job documents, manufacturer information, engineering review, or a qualified human decision.
Operating Mode | Low Temp Split (°F) | High Temp Split (°F) | Review or Entry Setting | Editable Value | Unit or Use
Cooling | 14 | 24 | Voltage variance limit | 10% | Percent of rated voltage
Heating | 20 | 50 | Running amps maximum ratio | 100% | Percent of nameplate amps
Fan Only |  |  | Minimum temperature entry | -100 | °F
|  |  | Maximum temperature entry | 250 | °F
|  |  | Maximum voltage entry | 1000 | V
|  |  | Maximum current entry | 500 | A
|  |  | Maximum pressure entry | 1000 | psig
|  |  | Earliest startup date | 2025-01-01 | MM/DD/YYYY
|  |  | Latest startup date | 2028-12-31 | MM/DD/YYYY
Equipment Types |  | Operating Modes | Checklist Statuses |  | Admin Statuses | Responsibilities | Fictional Technicians
Split AC |  | Cooling | Complete |  | Signed Off | Installing Contractor | Avery Example
Heat Pump |  | Heating | Needs Review |  | Awaiting Sign-Off | Startup Technician | Jordan Sample
Packaged Unit |  | Fan Only | Not Applicable |  | Not Ready | Customer Representative | Casey Fiction
Gas Furnace |  |  | Pending |  |  | Other | Riley Placeholder
Air Handler
Rooftop Unit